# Recessed mounted wall louvre DucoGrille Solid G 30Z Large

Manufactured by: DUCO Ventilation & Sun Control

DucoGrille Solid G 30Z Large is a recessed mounted wall louvre with an extra large flange manufactured from extruded aluminium sections. The stackable louvre blades provide unparalleled rigidity. The perforated louvre blades act as an insect screen (2 types of perforation). The “Z”-shaped louvre blade produces a sleek design.

## Features:

* Louvre pitch: 37.50 mm
* Installation depth: 31.90 mm
* Section thickness: minimum 1.2 mm

|  |  |  |  |
| --- | --- | --- | --- |
|  | DucoGrille Solid G 30Z Large P1 | DucoGrille SolidG 30Z Large P2 | DucoGrille Solid G 30Z Large NP |
| Visual free area | 60 | 86 | 0 |
| Physical free passage | 34 | 48 | 0 |
| Flange width | 40 | 40 | 40 |

## Accessories (included):

|  |  |  |
| --- | --- | --- |
|  | Perforated louvre blades | Stainless steel insect screen |
|  | Insect screen | Bird protection | 2,3 x 2,3 mm | 6 x 6 mm | 20 x 20 mm |
| DucoGrille Solid G 30Z Large P1 | S |  |  |  |  |
| DucoGrille Solid G 30Z Large P2 |  | S | S | O | O |
| DucoGrille Solid G 30Z Large NP |  |  |  |  |  |
| S = Standard | O = Optional |  |  |  |  |

## Surface treatment:

* Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)
* Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate standard version:

|  |  |  |  |
| --- | --- | --- | --- |
|  | DucoGrille Solid G 30Z Large P1 | DucoGrille SolidG 30Z Large P2 | DucoGrille Solid G 30Z Large NP |
| K-factor inlet | 16,94 | 15,02 |  |
| K-factor outlet | 18,26 | 15,62 |  |
| Ce | 0,243 | 0,258 |  |
| Cd | 0,234 | 0,253 |  |

### Flow rate version "+ options":

|  |  |  |  |
| --- | --- | --- | --- |
|  | DucoGrille Solid G 30Z Large P1 | DucoGrille SolidG 30Z Large P2 | DucoGrille Solid G 30Z Large NP |
| K-factor inlet | 21,43 | 18,58 |  |
| K-factor outlet | 17,08 | 14,13 |  |
| Ce | 0,216 | 0,232 |  |
| Cd | 0,242 | 0,266 |  |

### Water resistance standard version:

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | v = 0 m-s | v = 0.5 m-s | v = 1 m-s | v = 1.5 m-s | v = 2 m-s | v = 2.5 m-s | v = 3 m-s | v = 3.5 m-s |
| DucoGrille Solid G 30Z Large P1 | B | C | C | D | D | D | D | D |
| DucoGrille Solid G 30Z Large P2 | C | C | C | D | D | D | D | D |
| DucoGrille Solid G 30Z Large NP |  |  |  |  |  |  |  |  |

### Water resistance version "+ options":

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | v = 0 m-s | v = 0.5 m-s | v = 1 m-s | v = 1.5 m-s | v = 2 m-s | v = 2.5 m-s | v = 3 m-s | v = 3.5 m-s |
| DucoGrille Solid G 30Z Large P1 | B | B | C | C | D | D | D | D |
| DucoGrille Solid G 30Z Large P2 | B | B | B | B | C | D | D | D |
| DucoGrille Solid G 30Z Large NP |  |  |  |  |  |  |  |  |

## Complies with or tested in accordance with the following standards:

* Qualicoat Seaside type A (if painted finish)
* Qualanod (if anodised finish)
* EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening
* EN 13030: water resistance and determination of Ce and Cd coefficients